## Inputs & Summary
Robinshaw / Wayside – Condition 3 Drainage Calculations
FEH point | TQ 31438 30005 (GB x=531438, y=130005)
FEH model | FEH22
House impermeable area | 122 | m² per house
Number of houses | 2
Restricted discharge | 1 | l/s per house
Climate change allowance | 0.4 | 40%
Existing attenuation tank | 3.5 | m³ per house
Key result
100-year + 40% CC critical duration | 45 min | required storage (m³) | 4.1237
Existing tank shortfall | 0.62374 | m³ per house
Combined storage if both houses discharge to one tank | 8.2475 | m³

## FEH22 Rainfall
Duration | Duration (hr) | 1.3-year depth (mm) | 31-year depth (mm) | 100-year depth (mm) | 31-year +40% (mm) | 100-year +40% (mm)
5 min | 0.083 | 3 | 11.1453 | 13.561 | 15.6034 | 18.9854
15 min | 0.25 | 5.1 | 20.2453 | 25.4453 | 28.3434 | 35.6234
30 min | 0.5 | 6.7843 | 27.0906 | 34.3063 | 37.9269 | 48.0289
45 min | 0.75 | 7.8843 | 31.4453 | 39.9517 | 44.0234 | 55.9323
1 hr | 1 | 8.6843 | 34.6906 | 44.1517 | 48.5669 | 61.8123
2 hr | 2 | 13.0843 | 41.676 | 51.9909 | 58.3463 | 72.7873
4 hr | 4 | 18.1 | 49.676 | 61.2456 | 69.5463 | 85.7438
6 hr | 6 | 21.2843 | 54.8306 | 67.5613 | 76.7629 | 94.5858
12 hr | 12 | 26.9 | 64.7003 | 80.7309 | 90.5804 | 113.0233
18 hr | 18 | 30.5843 | 71.4392 | 90.3238 | 100.0149 | 126.4533
24 hr | 24 | 33.4843 | 76.9142 | 98.1995 | 107.6798 | 137.4793

## 1yr approx
Duration | Duration (hr) | FEH depth (mm) | CC factor | Adjusted depth (mm) | Runoff volume (m³) | Discharge volume (m³) | Required storage (m³)
5 min | 0.083 | 3 | 1 | 3 | 0.366 | 0.2988 | 0.0672
15 min | 0.25 | 5.1 | 1 | 5.1 | 0.6222 | 0.9 | 0
30 min | 0.5 | 6.7843 | 1 | 6.7843 | 0.82768 | 1.8 | 0
45 min | 0.75 | 7.8843 | 1 | 7.8843 | 0.96188 | 2.7 | 0
1 hr | 1 | 8.6843 | 1 | 8.6843 | 1.0595 | 3.6 | 0
2 hr | 2 | 13.0843 | 1 | 13.0843 | 1.5963 | 7.2 | 0
4 hr | 4 | 18.1 | 1 | 18.1 | 2.2082 | 14.4 | 0
6 hr | 6 | 21.2843 | 1 | 21.2843 | 2.5967 | 21.6 | 0
12 hr | 12 | 26.9 | 1 | 26.9 | 3.2818 | 43.2 | 0
18 hr | 18 | 30.5843 | 1 | 30.5843 | 3.7313 | 64.8 | 0
24 hr | 24 | 33.4843 | 1 | 33.4843 | 4.0851 | 86.4 | 0
Critical duration | 5 min
Critical required storage (m³) | 0.0672
Existing tank (m³) | 3.5
Surplus/(shortfall) (m³) | 3.4328

## 30yr (31yr FEH)
Duration | Duration (hr) | FEH depth (mm) | CC factor | Adjusted depth (mm) | Runoff volume (m³) | Discharge volume (m³) | Required storage (m³)
5 min | 0.083 | 11.1453 | 1 | 11.1453 | 1.3597 | 0.2988 | 1.0609
15 min | 0.25 | 20.2453 | 1 | 20.2453 | 2.4699 | 0.9 | 1.5699
30 min | 0.5 | 27.0906 | 1 | 27.0906 | 3.3051 | 1.8 | 1.5051
45 min | 0.75 | 31.4453 | 1 | 31.4453 | 3.8363 | 2.7 | 1.1363
1 hr | 1 | 34.6906 | 1 | 34.6906 | 4.2323 | 3.6 | 0.63226
2 hr | 2 | 41.676 | 1 | 41.676 | 5.0845 | 7.2 | 0
4 hr | 4 | 49.676 | 1 | 49.676 | 6.0605 | 14.4 | 0
6 hr | 6 | 54.8306 | 1 | 54.8306 | 6.6893 | 21.6 | 0
12 hr | 12 | 64.7003 | 1 | 64.7003 | 7.8934 | 43.2 | 0
18 hr | 18 | 71.4392 | 1 | 71.4392 | 8.7156 | 64.8 | 0
24 hr | 24 | 76.9142 | 1 | 76.9142 | 9.3835 | 86.4 | 0
Critical duration | 15 min
Critical required storage (m³) | 1.5699
Existing tank (m³) | 3.5
Surplus/(shortfall) (m³) | 1.9301

## 30yr +40CC
Duration | Duration (hr) | FEH depth (mm) | CC factor | Adjusted depth (mm) | Runoff volume (m³) | Discharge volume (m³) | Required storage (m³)
5 min | 0.083 | 11.1453 | 1.4 | 15.6034 | 1.9036 | 0.2988 | 1.6048
15 min | 0.25 | 20.2453 | 1.4 | 28.3434 | 3.4579 | 0.9 | 2.5579
30 min | 0.5 | 27.0906 | 1.4 | 37.9269 | 4.6271 | 1.8 | 2.8271
45 min | 0.75 | 31.4453 | 1.4 | 44.0234 | 5.3709 | 2.7 | 2.6709
1 hr | 1 | 34.6906 | 1.4 | 48.5669 | 5.9252 | 3.6 | 2.3252
2 hr | 2 | 41.676 | 1.4 | 58.3463 | 7.1183 | 7.2 | 0
4 hr | 4 | 49.676 | 1.4 | 69.5463 | 8.4847 | 14.4 | 0
6 hr | 6 | 54.8306 | 1.4 | 76.7629 | 9.3651 | 21.6 | 0
12 hr | 12 | 64.7003 | 1.4 | 90.5804 | 11.0508 | 43.2 | 0
18 hr | 18 | 71.4392 | 1.4 | 100.0149 | 12.2018 | 64.8 | 0
24 hr | 24 | 76.9142 | 1.4 | 107.6798 | 13.1369 | 86.4 | 0
Critical duration | 30 min
Critical required storage (m³) | 2.8271
Existing tank (m³) | 3.5
Surplus/(shortfall) (m³) | 0.67292

## 100yr
Duration | Duration (hr) | FEH depth (mm) | CC factor | Adjusted depth (mm) | Runoff volume (m³) | Discharge volume (m³) | Required storage (m³)
5 min | 0.083 | 13.561 | 1 | 13.561 | 1.6544 | 0.2988 | 1.3556
15 min | 0.25 | 25.4453 | 1 | 25.4453 | 3.1043 | 0.9 | 2.2043
30 min | 0.5 | 34.3063 | 1 | 34.3063 | 4.1854 | 1.8 | 2.3854
45 min | 0.75 | 39.9517 | 1 | 39.9517 | 4.8741 | 2.7 | 2.1741
1 hr | 1 | 44.1517 | 1 | 44.1517 | 5.3865 | 3.6 | 1.7865
2 hr | 2 | 51.9909 | 1 | 51.9909 | 6.3429 | 7.2 | 0
4 hr | 4 | 61.2456 | 1 | 61.2456 | 7.472 | 14.4 | 0
6 hr | 6 | 67.5613 | 1 | 67.5613 | 8.2425 | 21.6 | 0
12 hr | 12 | 80.7309 | 1 | 80.7309 | 9.8492 | 43.2 | 0
18 hr | 18 | 90.3238 | 1 | 90.3238 | 11.0195 | 64.8 | 0
24 hr | 24 | 98.1995 | 1 | 98.1995 | 11.9803 | 86.4 | 0
Critical duration | 30 min
Critical required storage (m³) | 2.3854
Existing tank (m³) | 3.5
Surplus/(shortfall) (m³) | 1.1146

## 100yr +40CC
Duration | Duration (hr) | FEH depth (mm) | CC factor | Adjusted depth (mm) | Runoff volume (m³) | Discharge volume (m³) | Required storage (m³)
5 min | 0.083 | 13.561 | 1.4 | 18.9854 | 2.3162 | 0.2988 | 2.0174
15 min | 0.25 | 25.4453 | 1.4 | 35.6234 | 4.3461 | 0.9 | 3.4461
30 min | 0.5 | 34.3063 | 1.4 | 48.0289 | 5.8595 | 1.8 | 4.0595
45 min | 0.75 | 39.9517 | 1.4 | 55.9323 | 6.8237 | 2.7 | 4.1237
1 hr | 1 | 44.1517 | 1.4 | 61.8123 | 7.5411 | 3.6 | 3.9411
2 hr | 2 | 51.9909 | 1.4 | 72.7873 | 8.88 | 7.2 | 1.68
4 hr | 4 | 61.2456 | 1.4 | 85.7438 | 10.4607 | 14.4 | 0
6 hr | 6 | 67.5613 | 1.4 | 94.5858 | 11.5395 | 21.6 | 0
12 hr | 12 | 80.7309 | 1.4 | 113.0233 | 13.7888 | 43.2 | 0
18 hr | 18 | 90.3238 | 1.4 | 126.4533 | 15.4273 | 64.8 | 0
24 hr | 24 | 98.1995 | 1.4 | 137.4793 | 16.7725 | 86.4 | 0
Critical duration | 45 min
Critical required storage (m³) | 4.1237
Existing tank (m³) | 3.5
Surplus/(shortfall) (m³) | -0.62374