## External Outline Specification
NBS | Item | description | Colours / Range | manufacturer
| Floor - Plant room | Floor thickness = 220mm (excluding structure) • Plant Room Paint Flooring. • 80mm Granolithic screed • Separation layer • 140mm Void Former • DPM • In-situ RC floor slab (subject to SE detailing) Note: Final floor build up subject to u-value calculations by insulation supplier; depth of void former to match
| Floor - Bin store and external plant enclosure | Concrete slab as per SE details. Brushed concrete finish
| External walls - Type 1 (General) | Standard wall thickness = 499.5mm • 102.5mm Facing Brickwork • 50mm unvented cavity • 160mm Mineral Wool Insulation • Breather Membrane • 12mm A1 Rated Cementitious Sheathing Board • 150mm SFS frame; 120mm Rockwool Steel Frame Slab Insulation • VCL (A2 rated) • 2x12.5mm GTEC Standard Board¹ Facing brick to be in two different colours as per planning elevations. Smooth precast parapet capping & string course. Note: Final wall thickness subject to u-value calculations by insulation supplier | Birtley Olde English Buff A2605A with light Buff Mortar or similar in stretcher bond. Bexhill Red A4010A light Buff Mortar or similar in stretcher bond. Physical sample will be delivered to Planning Authority. | Ibstock
| External walls - Type 2 (plantroom) | Standard wall thickness = 497mm • 100mm concrete masonry • 50mm unvented cavity • 160mm Mineral Wool Insulation • Breather Membrane • 12mm A1 Rated Cementitious Sheathing Board • 150mm SFS frame; 120mm Rockwool Steel Frame Slab Insulation • VCL (A2 rated) • 2x12.5mm GTEC Standard Board¹ Smooth precast parapet capping & string course. Note: Final wall thickness subject to u-value calculations by insulation supplier
| External walls - Type 3 (Bin store & external plant) | Open top timber slat enclosure, Western Red Cedar, with galvanised steel supports. Timber clad gates with standard hinges to be incorporated with lock. All timber to be FSC certified and sourced from sustainable forestry schemes. | Euroguard Combi Welded Mesh Panel | Jacksons Fencing
| External walls - Type 4 (Curtain walling) | High performance curtain wall system comprising thermally broken aluminium framing with low-emissivity glazing to meet U-value and solar heat gain coefficient requirements. System to be fully watertight, incorporating air and water barriers, and designed to accommodate wind loads, building movement, and thermal expansion in line with structural specifications. All components, including framing gaskets, and sealants to be corrosion resistant and durable. | RAL 1019 | Comar Architectural Aluminium Systems: https://www.comar-alu.co.uk/curtain-walling/ Smart Architectural Aluminium: https://www.smartsystems.co.uk/product/162/mc-600
| Roof - Type 1 (General) | Roof thickness = 205mm Overall thickness = 405mm • 1.5mm Bauder Thermofol PVC on 2mm fleece • 3mm Underlayer • 180mm PIR Insulation (insulation thickness subject to u-value calcs with manufacturer) • 2mm AVCL layer • 18mm WBP Plywood • 200mm Steel Roof Deck; falls determined by structural steelwork (depth subject to SE confirmation) Note: Where roof area is above a fire hazard room, fire rated plasterboard ceiling to be installed to u/s of steel deck. Note: Surface finishes to impose minimum load of 80KG/m2 to resist wind uplift and flotation. Note: Extent and loading of solar panels to be determined. | N/A | SMD Structural Floor and Roof Solutions: https://smdltd.co.uk/products-services/floor-deck/ Bauder Thermofol PVC System: https://www.bauder.co.uk/flat-roof-solutions/single-ply-roofing-systems/thermofol-pvc-system
| Roof - Type 2 (Canopy) | Same as above, with the inclusion of a decorative aluminium soffit RAL 1019 | RAL 1019 | As above
| Roof drainage | 300m Hoppers with outlets and rainwater downpipes. Aluminium powder coated. | RAL 1019
| Ladders | Access ladder to roof to comply with BS 4211:2005+A1:2008. Galvanised steel finish with lockable ladder cage. | Galvanised steel
| Balustrades | 1100mm high proprietary self-supporting balustrade with a galvanised steel finish, to meet lateral load requirements and to withstand external weather conditions. | Galvanised steel
| External soffits | Aluminium rainscreen cassettes with a powder coated finish RAL 1019. Feature flush downlights to meet lux levels as per MEP design. | RAL 1019
| External doors (General) | Curtain walling system as described above. | RAL 1019 | As curtain walling (line 7)
| External doors (Plant room) | Aluminium insulated double leaf doors, powder coated finish RAL 1019 | RAL 1019
| External louvres (Plant room) | Aluminium external louvres, powder coated finish RAL 1019 | RAL 1019
| Windows | High performance window comprising thermally broken aluminium framing with low-emissivity glazing to meet U-value and solar heat gain coefficient requirements. System to be fully watertight, incorporating air and water barriers, and designed to accommodate wind loads, building movement, and thermal expansion in line with structural specifications. All components, including framing gaskets, and sealants to be corrosion resistant and durable. All openable windows must be fitted with 100mm restrictors. | RAL 1019 | As curtain walling (line 7)
| Windows with insulated metal panels | High performance window comprising thermally broken aluminium framing with low-emissivity glazing to meet U-value and solar heat gain coefficient requirements. System to be fully watertight, incorporating air and water barriers, and designed to accommodate wind loads, building movement, and thermal expansion in line with structural specifications. All components, including framing gaskets, and sealants to be corrosion resistant and durable. Openable windows shall be integrated with insulated metal spandrel panels as per the planning elevations. All openable windows must be fitted with 100mm restrictors. | RAL 1019 | As curtain walling (line 7)
| Handrails | Metal railing PPC finished to external stairs and ramps. | RAL 1019
| Pergola | Western red cedar 200x200mm square sections, supported on galvanised steel footings. Timber shall be treated for outdoor use with an UV-resistant protective coating. All fasteners, including screws and brackets shall be made of stainless steel to prevent rust and corrosion. | Western red cedar | Accoya Simpson
| Modular cycle shelter | Fully open at all sides with powder coated steel structure and polycarbonate roof to accommodate 6 Sheffield stands. Stainless steel bike hoops to secure bikes. | RAL 1019 | Slingsby
| Bin store | Open top timber slat enclosure, Western Red Cedar, with galvanised steel supports. Timber clad gates with standard hinges to be incorporated with lock. All timber to be FSC certified and sourced from sustainable forestry schemes. | Euroguard Combi Welded Mesh Panel | Jacksons Fencing
| Fencing | Open top timber slat enclosure, Western Red Cedar, with galvanised steel supports. Timber clad gates with standard hinges to be incorporated with lock. All timber to be FSC certified and sourced from sustainable forestry schemes. | Euroguard Combi Welded Mesh Panel | Jacksons Fencing
| External paving - Concrete block paving | 300x150x100mm textured granite aggregate, mid-grey and graphite (colour locations as per landscape drawings). Manufactured to BS EN 1338. Square edged, laid to a stretcher bond with sand jointing. | Mid-grey and graphite | Marshalls Tobermore
| External paving - Concrete flag paving | Hard wearing, textured granite aggregate finish, 400x400x40mm. Silver / graphite colour. Manufactured to BS EN 1339:2003. Installed to BS 7533-4:2006. Chamferred edges. | Silver / Graphite | Marshalls Tobermore
| External paving - Tactile flag paving | 400x400x50mm buff coloured. Rib - type R1 to DD CEN/TS 15209. Laid in accordance with BS7533-4. Square edged and laid to stack bond with mortar jointing. | Buff | Marshalls Tobermore
| Edges | Concrete edges to paths: 150x50x915 precast concrete PN kerb smooth finished. Manufactured to BS EN 1339:2003 installed to BS 7533-6:1999. Chamferred edges. | Concrete
| Edges | Steel edges to planters: 300x5mm powder coated mild steel with tensile strenght of 430-550 Mpa and a hardness of 120-180 HB. Life expectancy of at least 20 years.
| External furniture (Tables and benches) | Galvanised steel frame with smooth-planed iroko timber slats. Manufactured to BS EN 1090-2-2018. Installed to BS 1722-11:2006.

## Internal Outline Specification
NBS | Item | description | Colours / Range | manufacturer
1 | General | Look and Feel. Overall appearance and look and feel to be agreed with the Users. Complimentary palettes of materials to be selected which also meets AD M requirements, and BREEAM requirements. A change from one manufacturer to another can have a significant knock on effect to the carefully considered overall look and feel of the building.
2 | IPC | Infection Prevention Control is a paramount consideration. Finishes should be non-organic, easy cleanable and interfaces between products / finishes should not leave any non-cleanable gaps.
K10 | Partitions | Typically 2x 12.5mm Acoustic Plasterboard, each side of 90mm 'C' stud with 50mm Mineral Wool Insulation between studs. ~ Ply pattressing between studs to support known fixings and to future proof likely fixings. ~ Extent of ply subject to Fire Engineer considerations. ~ Actual partition specification subject to acoustic consultant advice, fire officer requirements and tested system. |  | 1) Speedline metal 2) BG boards
K30 | Glass partition systems | Glass partition system as per GA plans |  | 1) SAS International 2) Komfort
K32 | IPS | Integrated Plumbing Systems for Clinical Wash hand basins, sanitaryware generally. |  | 1) Total Laminate Systems 2) Vepps Hygen, Venesta 3) Hygipods, Trovex 4) TBS Amwell 5) Bushboard
K40 | Ceilings | Solid plasterboard to pressure regime rooms, and non-observable patient areas (wcs showers) Dropped ceilings to feature areas, bulkheads. |  | 1) SpeedLine Drywall Systems 2) British Gypsum 3) Siniat
K40 | Ceilings | Lay in grid ceilings; tegular fittings. No cut tiles and plasterboard margins to (corridors and waiting areas) | Large format to corridors (1200 x 600). Standard 600 x 600 elsewhere. | Clincal areas 1) Bioguard Acoustic by Zentia (formerly Armstrong) 2) MediCare Plus by Rockfon Non-Clinical 1) Dune by Zentia 2) MediCare Standard Acoustic 1) Washable acoustic ceiling panels, Ecophon in bed bays.
L20 | Movable Wall | N/A
L20 | Doors | Timber doorsets throughout to be solid core and uPVC wrapped in selected locations. To be confirmed with IPC and FM teams. ~ contrasting leading edge door colour. ~ Leading edge protection to high traffic doors or those likely to receive impact from trolleys. ~ Option for uPVC wrapped architraves. ~ Privacy screens in glazing as required. | Project design. Fire Accreditation: BM Trada Q Mark or Certifire. | 1) Trovex 2) Specialist Door Solutions 3) Integrated Doosets (IDSL) 4) Ahmara Door Solutions 5) EDSi (uPVC wrapped doors)
L20 | Sliding Glass Doors | N/A
M50 | Flooring | Vinyl flooring throughout. 100mm coved skirting. Flooring to be within 10LRV throughout. ~ Heterogenous and homogenous require different cleaning products. Generally Trust preference to stick with one. ~ Safety flooring to wet areas, smooth finish elsewhere. ~ Electrostatic flooring to IT Hub and Switch Room Capping strips to be colour co-ordinated to ensure 30LRV difference between floor covering and walls. Matt wells to lobbies at both entrances Floor thickness = 220mm (excluding structure) • 2.5mm Vinyl Flooring • 2.5mm Latex Levelling Screed • 75mm screed • Separation layer • 140mm PIR Insulation • DPM • In-situ RC floor slab (subject to SE detailing) Note: Final floor build up subject to u-value calculations by insulation supplier | Project Design | 1) Desso Essence Carpet Tiles 2) Polysafe 3) Polyflor 4) Heckmondwike matting
M50 | Paint |  | Project design. Generally different themes to separate areas and to balance clinical environment with non-institutional design | 1) Johnstones Microbarr Antimicrobial Acrylic Matt 2) Dulux Sterishield.
N10 | Clinical Cabinetry | To accommodation modular inserts of baskets / shelves. Lockable doors. Worktops with 'C' channel uPVC colour matched edging. Infill panels to underside of ceilings and to adjacent walls or sloping top boxes. | Standard white or light grey. | 1) Stirling Medical 2) Hygenius (Work Space Design) 3) Medstor 4) Bristol Maid for Drugs Cupboards 5)David Bailey 6) Medspace
N10 | Non-Clinical cabinetry | Standard domestic kitchen range, typically high gloss. Staff kitchenette for example, visitors waiting areas. Soft close doors / drawers. Infill panels to u/s ceiling and adjacent walls or sloping top boxes. | TBC | 1) Howdens 2) others
N10 | Worktops | Laminate worktops with 'C' uPVC lipping, cantilevered legs to office areas. Stirling 40mm HP laminate worktops c/w Bullnose front profile. | project design. | 1) Stirling Medical 2) Hygenius (Work Space Design) 3) Medstor 4) Bristol Maid for Drugs Cupboards 5)David Bailey 6) Medspace
N10 | Shelving | Solid grade laminate shelves, with bevelled from edge on heavy duty brackets on Spurlok shelving or similar. Depth, 300mm, 450mm or 600mm subject to use.
N10 | Reception Desks | Upstands and carcasses to be laminate faced with 2mm uPVC lippings. | project design. | 1) Receptek 2) Hygenius (Work Space Design) 3) others
N11 | Hot Water Boiler | Zipp Hydro Tap, worktop mounted with boiling water. To Mini kitchen (staff rest room)
N11 | Ward Pantry | N/A
N13 | Sanitaryware; Clinical | Clinical WHB: S0430(HY) Contour 21+ 50cm back outlet washbasin, no tapholes, anti-splash and anti-microbial glaze. Tap: ~ Horne Optitherm tap (TBT1 200DL) (Kingston Specification Sept 2022). ~ Note, other trusts moving away from Horne to; ~~ A6682(AA) (TB H2A) Markwik 21+ panel mounted thermostatic basin mixer, single sequential lever, demountable with detachable spout, or ~~ Handwash - Clinical TMV Delabie Securitherm Bioclip themostatic basin mixer panel mounted thermostatic basin mixer, single sequential leverRef. H9614p, or ~~ Handwash - Clinical Non-TMV Delabie Sequential mechanical basin mixer panel mounted, single sequential leverRef. 2644P |  | WHB - Ideal Standard Tap - Horne Engineering Other sanitaryware - Ideal Standard; Contour 21+ / Markwik range, Delabie
N13 | Sanitaryware; Patient WCs in ensuites / assisted showers. | N/A
N13 | Sanitaryware; WCs | WC-Wheelchair Armitage Shanks, Contour 21+ 70cm projection back to wall rimless WC pan with horizontal outlet and anti-microbial glaze. Ref. S0437(HY) WC -Ambulant Armitage Shanks, Contour 21+ raised height back to wall rimless WC pan with raised horizontal outlet and anti-microbial glaze. Ref. S0440(HY) | Colour contrasting seat.
N13 | Sanitaryware; Shower | Shower - Shower Horne, TSV1-3 Shower Panel with Lever Controls, Integral ILTDU and Pipe Cover.Ref. Horne T105T92L
N13 | Grabrails | Wheelchair accessible WCs. 1x hinged grabrail, S6360(RN) Contour 21 hunged arm wall support rail. 5x 600mm straight grabrail, S6454(RN) Contour 21 grab rail straight 60cm long. (2x vertical by WHB, 2x vertical by WC, 1x horizontal to rear of door. 1x 450mm grabrail to wall by WC, S6452(RN) Contour 21 grab rail straight. For Assisted WCs, OMIT 1x 450mm grab rail, ADD 1x hinged grabrail.
N13 | Changing places | Equipment as per guidance |  | Scanflex, Innova
N14 | Signage - Internal | Door iD signage; acyic with VHB adhesive tape to rear. Typically 40mm high x strong length. Room Name signage; Trust preference. |  | 1) DMA Signs 2) X Sign
P20 | Wall Protection | uPVC wall protection; ~ Full height to; dirty utility, clean utility, near patient test, shower, WCs. ~ Half height to corridor, equipment parking bays, stores ~ Splashback; Clinical worktops, staff kitchennette worktops. Colour matched hot weld joints Smooth / stippled finish to be agreed with IPC. | White - predominate use Pastels - soft hues Vibrant - accent colours for key areas | 1) Trovex 2) Altro 3) CS Acrovyn 4) Yeoman Shield
P20 | Wall Protection, Crash Barriers | Aluminium retainer with uPVC encapsulation, with integrated or separate handrail. |  | 1) CS Acrovyn 2) Yeoman Shield 3) Gradus
P20 | Wall Protection, Corner Guards | Corner protection from impact of trolleys. Aluminium screw fixed retainer with uPVC wrap cover. | Standard colour range; white / grey | 1) CS Acrovyn 2) Yeoman Shield 3) Gradus
Z22 | Mastic | Polyurethane mastic to seal joints between materials / surfaces. Between joinery wand walls, wall protection and walls, cabinetry and floor / walls, IPS to floor / walls, electric face plates to walls (in clinical areas), dado trunking to walls, vinyl capping strip to walls, worktops to walls, doors frame and architraves to walls and floors, windows to walls, etc. | clear, white and grey; colour matched to feature splashbacks.
| Macerator | Vortex by Vernacare